# Village of Schuylerville / Village of Victory Water Board

### Meeting Minutes

Date: March 16, 2026
Location: Village of Victory

## 1. Call to Order & Pledge

The meeting was called to order and the Pledge of Allegiance was recited.

## Attendance

Members present included:

Chairman Drew

Commissioner Campbell

Commissioner Dennison

Commissioner Healy

Secretary Jamie Porter

## 2. Board Announcements

- The next Water Board meeting is scheduled for April 20, 2026 @ 6:00 PM following the public hearing at the Village of Victory meeting hall

## 3. Approval of Previous Minutes

- Motion: Approve February 2026 meeting minutes made by Commissioner Dennison

- Seconded by: Commissioner Campbell

## 4. Treasurer’s Report (as of February 28, 2026)

- Operating Account: $134,171.56

- NYCLASS Operating: $106,311.51

- NYCLASS Filter: $227,982.08

- NYCLASS Capital: $65,425.54

## 5. Plant & Operations JCF Report

Key operational issues and updates included:

- RO System Issues (RO1):

  - Multiple low inlet pressure alarms occurred on March 5–6 Schuylerville plant.

  - Pre-filters were replaced, restoring temporary operation.

  - Continued issues led to shutdown of RO1 and operation on RO2.

  - Inspection revealed:

    - Membranes clogged with rust and filter debris.

  - Membranes were cleaned and reassembled.

  - System now operational, though intermittent issues persist due to a faulty ROS valve.

  - Action: Clean or replace ROS valve components (solenoid/actuator) if problems continue.

### Well System Maintenance

- Well #2 Repair:

  - Leak identified in threaded couplings.

  - Pipe disassembled, rethreaded, and reassembled.

  - System restored to full operation.

  - Contractor (Mark Rogers) did not charge for repair labor.

- Ongoing Concern:

  - Additional evaluation needed for Victory plant well performance.

  - Action: Schedule further inspection with Mark Rogers.

### UV Disinfection System

- UV system alarm triggered during well work.

- Troubleshooting steps:

  - Components cleaned/replaced.

  - Electrical diagnostics conducted with manufacturer support.

- Determination:

  - Failed ground fault sensor.

- Quote Received: $508.90 for replacement sensor (Novex).

- Issue: Part is backordered until mid-April.

- Action: Proceed with replacement upon availability.

### Generator Maintenance

- Cummins serviced three generators:

  - No operational issues identified.

  - Batteries replaced in all units.

- Discussion raised regarding:

  - Existing service contract nearing expiration (~5-year term).

  - Potential cost savings by switching to a local provider (Conover).

- Action: Review contract status and obtain alternative quotes before renewal.

### Chemical Feed System

- Sodium Permanganate System:

  - Injection system required cleaning.

  - No spare check valves available at time of repair.

  - Replacement parts ordered.

  - Cleaned components currently functioning.

- Action: Replace components upon failure and maintain spare inventory.

### Regulatory Reporting

- Annual Water Report (AWR):

  - In progress for Department of Health submission.

- Water Withdrawal Report:

  - In progress for NYS DEC.

  - Due by March 31, 2026.

### RO Filter Procurement

- Three quotes obtained for RO2 filters.

- Proposal to purchase 200 filters to cover:

  - Quotes VEOLIA- drum of KLEEN Motion approved by Commissioner Healy, motion seconded by Commissioner Dennison to approve

  - Quotes VEOLIA Membrane filters Motion approved by Commissioner Healy, motion seconded by Commissioner Dennison

  - UV sensor purchase - Motion approved by Commissioner Healy, motion seconded by Commissioner Dennison

### Pressure Vessels

- Quote received for:

  - Replacement pressure vessels

  - Associated piping and valves

  - New PLC system

- Information distributed for review.

- Action: Further evaluation required before decision.

### Emerging Technology – Lead Service Line Identification

- Presentation attended on electric resistivity testing (Electroscan technology):

  - Non-invasive internal pipe scanning via probe.

  - Identifies pipe material (lead, copper, plastic, etc.) with high accuracy.

- Key insights:

  - Estimated cost: $200–$700 per property

  - Compared to potholing: up to $5,000 per property

  - EPA now requires verification at:

    - Interior plumbing

    - Curb stop

    - Main connection

- Regulatory implications:

  - Full lead service line replacement required by ~2037–2039.

  - Excavation methods now considered “disturbances,” triggering:

    - Flushing protocols

    - Filter distribution requirements.

- Vendor may assist with grant funding opportunities.

- Action:

  - Gather additional information and evaluate as a potential compliance strategy.

## 6. Old Business

### Water Line Data Collection

- Ongoing effort to collect missing service line data.

- Some addresses found to be invalid.

### Email System Transition

- Cost: $1,242.22 (3 years).

- Issue: Water Board lacks credit card.

Decision / Direction:

- Proceed via Village credit card and reimburse if allowed

### Inventory & Equipment Issues

- Approximately $3,000 in obsolete fittings identified.

- Discussion of:

  - Scrapping or surplus sale (GovDeals).

  - Maintaining better inventory records going forward.

### Material Policy – Plastic vs Copper

- No single material mandated.

- Determination will be job-specific.

Decision:

- Continue using both materials based on conditions.

## 7. Equipment Purchases

### Approved Purchases

- Portable generator (~$600)

- Trash pump (~$900)

Motion made to approve purchases by Commissioner Campbell seconded by Commissioner Dennison

### Deferred / Future Considerations

- Jumping jack (compactor)

- Additional equipment list

- Trailer replacement

- Storage improvements

## 8. Trailer & Storage Discussion

- Existing trailer:

  - Poor condition

  - Mold present

  - Roof leaking

- Considerations:

  - Replacement trailer

  - Covered storage (lean-to or structure)

  - Potential relocation to Victory plant

## 9. Fence Repairs

  - Replace hardware and realign gate (Schuylerville plant)

  - Repair top rail (Victory plant)

- Motion: Approve repairs not to exceed $800 made by Chairman Drew and seconded by Commissioner Campbell

## 10. Capital Planning & System Capacity Discussion

- Discussion of:

  - Potential expansion

  - Re-activating secondary well (noting PFAS concerns)

## 10. Budget & Public Hearing

- Discussion on scheduling public hearing prior to regular meeting at 6:00 pm Village

## 11. Approval of Vouchers-

- Commissioner Dennison made the motion to approve the Vouchers in the amount of $22,296.12 Commissioner Campbell 2nd the motion to approve.

## 12. Adjournment

- Meeting adjourned following completion of business.

- Motion to adjourn made by Commissioner Campbell motion 2nd by Chairman Drew

Respectfully submitted by

Jamie Porter

Water Board Secretary